## in
| The location of the model's DLL (example ..\test.dll) (DLLFile) | P_VLLbase - RMS L-L base voltage (P_VLLbase) | P_Sbase - VA base (P_Sbase) | P_Tflt_v - LPF time constant for voltage (P_Tflt_v) | P_Vflt_flag - Flag for voltage filter (P_Vflt_flag) | P_Tflt_i - LPF time constant for current (P_Tflt_i) | P_Iflt_flag - Flag for currrent filter (P_Iflt_flag) | P_Cur1_flag - Flag for current selection (1: current control before LCL, 0: current control after LCL) (P_Cur1_flag) | P_k_PLL - Damping constant for SOGI filter (P_k_PLL) | P_KpPLL - Proportional gain for PLL (P_KpPLL) | P_KiPLL - Integral gain for PLL (P_KiPLL) | P_Lim_PLL - Windup limit for PLL (P_Lim_PLL) | P_w_nom - Nominal angular frequency (P_w_nom) | P_tstart_up - Time for start up flag of Q and Vt closed loop (P_tstart_up) | P_Vdc_nom - Nominal DC Link Voltage (P_Vdc_nom) | P_VI_flag - 1: enable PPS VI characteristic, 0: constant I (P_VI_flag) | P_MPPT_flag - 1: enable MPPT for Vdc*, requires VI_flag=1 and Vdc_flag=1 (P_MPPT_flag) | P_b_Vdc - Setpoint weight for DC voltage (P_b_Vdc) | P_Kp_Vdc - Proportional gain for Vdc (P_Kp_Vdc) | P_Ki_Vdc - Integral gain for Vdc (P_Ki_Vdc) | P_T_frq - Time constant for PLL frequency (P_T_frq) | P_fdbd1 - Lower deadband for frequency droop control (P_fdbd1) | P_fdbd2 - Upper deadband for frequency droop control (P_fdbd2) | P_Ddn - Inverse of droop for high frequency (P_Ddn) | P_Dup - Inverse of droop for low frequency (P_Dup) | P_Tp_droop - Time constant for first order lag block in P-f control (P_Tp_droop) | P_Vdc_flag - Vdc control flag (1: enable, 0: const. PQ) (P_Vdc_flag) | P_f_flag - Frequency flag (1: enable frequency droop control) (P_f_flag) | P_Id_frz_flag - freeze Id during LVRT (P_Id_frz_flag) | P_Ilim_pu - Inverter Current limit (P_Ilim_pu) | P_Vt_ref - pu reference voltage for Vt control (P_Vt_ref) | P_Kv_p - Proportional gain for terminal voltage PI controller (P_Kv_p) | P_Kv_i - Integral gain for terminal voltage PI controller (P_Kv_i) | P_Qmin - Minimum reactive power in pu (P_Qmin) | P_Qmax - Maximum reactive power in pu (P_Qmax) | P_Kq_p - Q closed-loop proportional control gain (P_Kq_p) | P_Kq_i - Q closed-loop integral control gain (P_Kq_i) | P_dbhv_frt - Dead band LVRT +ve sequence HV (P_dbhv_frt) | P_dblv_frt - Dead band HVRT +ve sequence LV (P_dblv_frt) | P_Kqv1 - Proportional gain for positive voltage dip (P_Kqv1) | P_Qctl_CL_flag - 1: enables closed loop Q control, 0: open loop (P_Qctl_CL_flag) | P_Vt_flag - 1: enable inverter term. voltage control, 0: Q control (P_Vt_flag) | P_dbl_2 - VRT dead band (negative) (P_dbl_2) | P_dbh_2 - VRT dead band (positive) (P_dbh_2) | P_Kqv2 - Proportional gain for -ve voltage deviation (P_Kqv2) | P_V2_flag - 1: enable V2 control during FRT (P_V2_flag) | P_Ipramp_up - Ramp up rate for active current (P_Ipramp_up) | P_Kcc_p - Proportional gain PI controller in current controller (P_Kcc_p) | P_Kcc_i - Integral gain PI controller in current controller (P_Kcc_i) | P_Lim_upCC - Current controller's anti-windup upper limit (P_Lim_upCC) | P_Lim_lowCC - Current controller's anti-windup lower limit (P_Lim_lowCC) | P_Tau_Vff - Time constant of LPF for voltage current controller (P_Tau_Vff) | P_Vff_flag - Voltage feed-forward flag (1: enable) (P_Vff_flag) | P_Lchoke - Filter inductance (P_Lchoke) | P_IR_flag - Flag (P_IR_flag) | TRelease - Time to Release Initial Conditions (sec) (TRelease) | O_m_ainit - Initial Value of Output (O_m_ainit) | O_m_binit - Initial Value of Output (O_m_binit) | O_m_cinit - Initial Value of Output (O_m_cinit) | O_FreqPLLinit - Initial Value of Output (O_FreqPLLinit) | O_Output_1init - Initial Value of Output (O_Output_1init) | O_Output_2init - Initial Value of Output (O_Output_2init) | O_Output_3init - Initial Value of Output (O_Output_3init) | O_Output_4init - Initial Value of Output (O_Output_4init) | O_Output_5init - Initial Value of Output (O_Output_5init) | O_Output_6init - Initial Value of Output (O_Output_6init) | O_Output_7init - Initial Value of Output (O_Output_7init) | O_Output_8init - Initial Value of Output (O_Output_8init) | O_Output_9init - Initial Value of Output (O_Output_9init)
1388815360 | ..\DLL_new.dll | 600 | 1000000 | 1e-05 | 1 | 1e-05 | 1 | 1 | 1 | 25.4 | 324 | 70 | 376.9911 | 1.9 | 1200 | 0 | 0 | 0.56 | 5.18 | 52.91 | 0.1 | -0.0006 | 0.0006 | 20 | 0 | 0.001 | 0 | 0 | 0 | 1.1 | 1.01 | 0 | 100 | -0.4 | 0.4 | 0 | 40 | -0.1 | 0.1 | 2 | 1 | 0 | -0.1 | 0.1 | 2 | 0 | 1 | 0.32325 | 324 | 99999 | -99999 | 0.0001 | 0 | 0.0001 | 1 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sheet1
| 1388815360 | EMTHub
The location of the model's DLL (example ..\test.dll) (DLLFile) | ..\DLL_new.dll
P_VLLbase - RMS L-L base voltage (P_VLLbase) | 600 | 600
P_Sbase - VA base (P_Sbase) | 1000000 | 1000000
P_Tflt_v - LPF time constant for voltage (P_Tflt_v) | 1e-05 | 1e-05
P_Vflt_flag - Flag for voltage filter (P_Vflt_flag) | 1 | 1
P_Tflt_i - LPF time constant for current (P_Tflt_i) | 1e-05 | 1e-05
P_Iflt_flag - Flag for currrent filter (P_Iflt_flag) | 1 | 1
P_Cur1_flag - Flag for current selection (1: current control before LCL, 0: current control after LCL) (P_Cur1_flag) | 1 | 1 | corrected from 0
P_k_PLL - Damping constant for SOGI filter (P_k_PLL) | 1 | 1
P_KpPLL - Proportional gain for PLL (P_KpPLL) | 25.4 | 25.4
P_KiPLL - Integral gain for PLL (P_KiPLL) | 324 | 324
P_Lim_PLL - Windup limit for PLL (P_Lim_PLL) | 70 | 70
P_w_nom - Nominal angular frequency (P_w_nom) | 376.9911 | 376.9911
P_tstart_up - Time for start up flag of Q and Vt closed loop (P_tstart_up) | 1.9 | 1.9
P_Vdc_nom - Nominal DC Link Voltage (P_Vdc_nom) | 1200 | 1200
P_VI_flag - 1: enable PPS VI characteristic, 0: constant I (P_VI_flag) | 0 | 0
P_MPPT_flag - 1: enable MPPT for Vdc*, requires VI_flag=1 and Vdc_flag=1 (P_MPPT_flag) | 0 | 0
P_b_Vdc - Setpoint weight for DC voltage (P_b_Vdc) | 0.56 | 0.56
P_Kp_Vdc - Proportional gain for Vdc (P_Kp_Vdc) | 5.18 | 5.18
P_Ki_Vdc - Integral gain for Vdc (P_Ki_Vdc) | 52.91 | 52.91
P_T_frq - Time constant for PLL frequency (P_T_frq) | 0.1 | 0.1
P_fdbd1 - Lower deadband for frequency droop control (P_fdbd1) | -0.0006 | -0.0006
P_fdbd2 - Upper deadband for frequency droop control (P_fdbd2) | 0.0006 | 0.0006
P_Ddn - Inverse of droop for high frequency (P_Ddn) | 20 | 20 | DDN
P_Dup - Inverse of droop for low frequency (P_Dup) | 0 | 0 | DUP
P_Tp_droop - Time constant for first order lag block in P-f control (P_Tp_droop) | 0.001 | 0.001
P_Vdc_flag - Vdc control flag (1: enable, 0: const. PQ) (P_Vdc_flag) | 0 | 0
P_f_flag - Frequency flag (1: enable frequency droop control) (P_f_flag) | 0 | 0 | FFLAG
P_Id_frz_flag - freeze Id during LVRT (P_Id_frz_flag) | 0 | 0
P_Ilim_pu - Inverter Current limit (P_Ilim_pu) | 1.1 | 1.1
P_Vt_ref - pu reference voltage for Vt control (P_Vt_ref) | 1.01 | 1.01 | Input Signal
P_Kv_p - Proportional gain for terminal voltage PI controller (P_Kv_p) | 0 | 0 | KV_P
P_Kv_i - Integral gain for terminal voltage PI controller (P_Kv_i) | 100 | 100 | KV_I
P_Qmin - Minimum reactive power in pu (P_Qmin) | -0.4 | -0.4
P_Qmax - Maximum reactive power in pu (P_Qmax) | 0.4 | 0.4
P_Kq_p - Q closed-loop proportional control gain (P_Kq_p) | 0 | 0 | KQ_P
P_Kq_i - Q closed-loop integral control gain (P_Kq_i) | 40 | 40 | KQ_I
P_dbhv_frt - Dead band LVRT +ve sequence HV (P_dbhv_frt) | -0.1 | -0.1
P_dblv_frt - Dead band HVRT +ve sequence LV (P_dblv_frt) | 0.1 | 0.1
P_Kqv1 - Proportional gain for positive voltage dip (P_Kqv1) | 2 | 2 | KQV1
P_Qctl_CL_flag - 1: enables closed loop Q control, 0: open loop (P_Qctl_CL_flag) | 1 | 1 | QCFLG
P_Vt_flag - 1: enable inverter term. voltage control, 0: Q control (P_Vt_flag) | 0 | 0 | VTFLG
P_dbl_2 - VRT dead band (negative) (P_dbl_2) | -0.1 | -0.1
P_dbh_2 - VRT dead band (positive) (P_dbh_2) | 0.1 | 0.1
P_Kqv2 - Proportional gain for -ve voltage deviation (P_Kqv2) | 2 | 2 | KQV2
P_V2_flag - 1: enable V2 control during FRT (P_V2_flag) | 0 | 0 | V2FLG
P_Ipramp_up - Ramp up rate for active current (P_Ipramp_up) | 1 | 1
P_Kcc_p - Proportional gain PI controller in current controller (P_Kcc_p) | 0.32325 | 0.32325
P_Kcc_i - Integral gain PI controller in current controller (P_Kcc_i) | 324 | 324
P_Lim_upCC - Current controller's anti-windup upper limit (P_Lim_upCC) | 99999 | 99999
P_Lim_lowCC - Current controller's anti-windup lower limit (P_Lim_lowCC) | -99999 | -99999
P_Tau_Vff - Time constant of LPF for voltage current controller (P_Tau_Vff) | 0.0001 | 0.0001
P_Vff_flag - Voltage feed-forward flag (1: enable) (P_Vff_flag) | 0 | 0
P_Lchoke - Filter inductance (P_Lchoke) | 0.0001 | 0.0001 | LCHOK
Rchoke |  | 0.00075 | RCHOK
P_IR_flag - Flag (P_IR_flag) | 1 | 1
TRelease - Time to Release Initial Conditions (sec) (TRelease) | 0.01 | 0.01 | corrected from 0.001
O_m_ainit - Initial Value of Output (O_m_ainit) | 0
O_m_binit - Initial Value of Output (O_m_binit) | 0
O_m_cinit - Initial Value of Output (O_m_cinit) | 0
O_FreqPLLinit - Initial Value of Output (O_FreqPLLinit) | 0
O_Output_1init - Initial Value of Output (O_Output_1init) | 0
O_Output_2init - Initial Value of Output (O_Output_2init) | 0
O_Output_3init - Initial Value of Output (O_Output_3init) | 0
O_Output_4init - Initial Value of Output (O_Output_4init) | 0
O_Output_5init - Initial Value of Output (O_Output_5init) | 0
O_Output_6init - Initial Value of Output (O_Output_6init) | 0
O_Output_7init - Initial Value of Output (O_Output_7init) | 0
O_Output_8init - Initial Value of Output (O_Output_8init) | 0
O_Output_9init - Initial Value of Output (O_Output_9init) | 0